# Operation

1.   Setup:

Insure that the sensor you are using:

a. Operates on 15 VDC to 18 VDC supply.

b. Consumes 100 mA or less of operating current

c. Has a sink or source output that is connected to Python’s TRIAC switch control line 		      on the version of connector that you choose (either output will activate the TRIAC).

NOTE: Miswiring can render the Python permanently non-functional.

2.  Connect Source Voltage and Load:

Caution:  Check specifications of Relay or PLC Input before connecting.  Relay or PLC Input load must be a Minimum 1200 ohm at 120 VAC / 2400 ohm at 240 VAC to prevent irreversible damage to the Python.

3.   Checkout:

Plug Python’s connector into sensor and check for proper function. When the sensor’s output

switch closes, Python’s TRIAC switch should close, energizing the applied load or PLC input.

# SPECIFICATIONS

##### AC Power Requirements

Supply voltage range      			100 VAC TO 240 VAC, 50/60Hz

Current and power consumption		38 mA max., 4VA max.

Installation category				II (IEC 60364-4-443)

Input fusing			              	Non-replaceable, non-repairable

##### DC Output Ratings (to sensor)

##### Output voltage @ rated current		15 VDC min.

##### Output voltage @ no load			20 VDC max.

##### Output voltage regulation			40 V/A

##### Output current, max. rated 			100 mA

##### Output current fault, max.			200 mA

##### Pri/sec. isolation				2200 VAC, 1 min.

##### Turn-on delay, 100 mA load, 90% final voltage	10 ms typical

##### Turn-off delay, 0 mA load, 10% full voltage	1 sec typical

##### TRIAC Switch Ratings (switch AC current only)

##### Features		Optically isolated, zero-crossing

##### Switch voltage, maximum			230 VAC

##### Switch current, maximum 			50 mA @ 230 VAC, 100 mA @ 120 VAC

Peak repetitive surge current			1 A (100µs, 120pps)

##### On-state voltage				3 V max @ 100mA

##### Off-state leakage				500 nA max.

##### Holding current				250 µA typ.

##### Critical rate of rise of off-state voltage		600 V/us min.

##### Isolation surge voltage			7500 VAC min, 60 Hz. 1sec.

##### Turn-on time, full load, max voltage		15 ms max. (zero-crossing)

##### Turn-off time, full load, max voltage		15 ms max. (zero-crossing)

##### Over-current protection			 Internal fuse (non-replaceable, non-repairable)

##### Minimum Load				1200 ohm at 120 VAC, 600 ohm at 240 VAC

##### Mechanical & Cables

##### Material					PVC

Body dimension, length x diameter		152 mm (6 in.) x 24 mm (0.95in.)

AC cable:   4-wire, 18AWG, 300V, PVC		2 m (79 in.) x 7 mm (0.28 in.) dia.

DC cable:   4-wire, 22AWG, 300V, PVC 		1 m (39 in.) x 5.2 mm (0.21 in.) dia.

##### Environmental

##### Operating temperature			-25°C to 60°C (-13°F to 140°F)

##### Storage temperature 			-40°C to 85°C (-40°F to 185°F)

Humidity					100%, non-condensing

##### Enclosure ratings				Type 1 (UL50), IP67

##### Approvals / Certifications

##### North Amer. Safety:		UL, UL-c		UL 61010C-1, “Industrial Control Equipment”

##### File #E238344

##### European safety:		CE		EN 61010C-1

##### North American emissions	FCC		Class A

##### EU emissions		CE		EN55011:1998 Group 1,  Class A

##### EU EMC					EN61326:1997 Measure, Lab., and Control

##### Materials safety		FDA		cables and over-mold are FDA compatible 						non-contact

DIMENSIONS

PYTHON POWERTM

# Diagnostics

1.  Everything is connected but sensor does not appear to operate:

a.	Disconnect sensor and check for proper DC output voltage at Python connector.

2.  Sensor is receiving power but does not actuate Python’s TRIAC switch:

a.	Python’s TRIAC is a floating switch. An external power source must be applied to 			the load circuit in which the TRIAC acts as switch. Be extremely careful not to allow 			currents greater than rated current to flow through the TRIAC switch or permanent 			damage may occur. An internal fuse may blow if current is applied in excess of the 			rating. The fuse is not replaceable.

3.   Python presents proper output voltage when disconnected from the sensor but will not  		correctly power the sensor when connected:

a.	The sensor may be drawing too much current causing Python’s output voltage to 			fall below a useful level.

b.	Excess output loading my also be caused by a load on the sensor’s PNP (sourcing) 			output line that, in addition to the sensor’s current requirement, exceeds capacity.

LIMITATIONS AND EXCLUSION OF WARRANTIES

All goods purchased from Hyde Park Electronics LLC. shall be free from defects in materials, design and workmanship under normal conditions of use for one year from the date of shipment.  THIS WARRANTY IS THE SOLE WARRANTY AND IS EXPRESSLY IN LIEU OF ALL OTHER WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY IMPLIED WARRANTY OF MERCHANTABILITY OF FITNESS FOR A PARTICULAR PURPOSE.  THE LIABILITY OF HYDE PARK TO ANY PURCHASER SHALL BE LIMITED EXCLUSIVELY TO THE COST OF REPLACEMENT OR REPAIR OF DEFECTIVE PARTS, AND SHALL NOT INCLUDE LIABILITY FOR ANY DIRECT, CONSEQUENTIAL OR INCIDENTAL DAMAGES WHATSOEVER, WHETHER FORESEEN OR UNFORESEEN, INCLUDING BUT NOT LIMITED TO LOST PROFITS, LOST SALES, OR INJURY TO PERSONS OR PROPERTY.

HYDE PARK ELECTRONICS LLC

1875 Founders Drive,   Dayton, Ohio  45420-4017

Phone (937) 252-2121   Fax (937) 258-5830

Email: help@sesensors.com      Web Site: http://www.sesensors.com

( 2004 Hyde Park Electronics LLC

##### XXZPM100M12 patent pending

##### Power Supply and TRIAC Switch Accessory

Python is an accessory that allows a DC sensor to be installed in locations where only AC power is available or to simply maximize installation efficiency. Python consists of a universal, in-line AC/DC power supply and TRIAC switch. The DC output will power most types of sensors. The TRIAC switch is controlled by the sensor’s standard sink or source output…Python automatically accepts either.

#### BRIEF SPECIFICATION

Input:		100-240 VAC, 50 / 60 Hz, 38 mA max., 3 VA

DC Output:	15 VDC min @ 100 mA, 20 VDC max @ no load

Switch:		Opto-isolated TRIAC, 50 mA @ 230 VAC (100 mA @ 120 VAC)

# Model Key

Model	   	     Connector              Female contacts       Pinout, cable connector

XXZAC137 	8-to-M12 cable: Use

Cable:                	to connect PM100-02

to 4-pin M8 sensors

XXZPM100M12	   12mm (Micro) - Sensor End       4

2 m cable - power end

XXZPM100L2	No Connector	 	     N/A

On Either End

Switch control = sink or source output from DC sensor

# Text boxes

SENSOR

AC/DC

TRIAC

L

N

AC

AC

CABLE

PM100-02

PYTHON POWER

CABLE

DC

DRIVING  POWER  RELAY

COM

15VDC

CONTROL

POWER

LOAD

RED/WHITE

RED/BLACK

VIOLET

YELLOW

SENSOR

AC/DC

TRIAC

PLC

AC

INPUTS

3

2

1

C

N

L

L

N

AC

AC

CABLE

PM100-02

PYTHON POWER

CABLE

DC

TYPICAL  PLC  CONNECTION

RED/WHITE

RED/BLACK

VIOLET

YELLOW

COM

15VDC

CONTROL

100mA

MAXIMUM

100mA

MAXIMUM

UNINTENDED OPERATION

Apply an AC Load that limits Python's TRIAC switch to rated current

Failure to follow this instruction can result in injury or equipment damage

CAUTION

HAZARD OF ELECTRIC SHOCK, EXPLOSION, OR ARC FLASH

Turn off power to this equipment before installation or removal

Consult and follow local and national electrical codes

Do not submerse in liquids for extended periods of time

Failure to follow these instructions will result in death or serious injury.

DANGER